## fouling_factors
Stream | fouling factors
Natural gas | 0.0002–0.0004
Column verhead products | 0.0002
Lean oil | 0.0004
Rich oil | 0.0002
Natural gasoline and liquefied petroleum gases | 0.0002
Atmospheric tower overhead vapors | 0.0002
Light Naphtha | 0.0004
Vacuum overhead vapors | 0.0008
SALT Crude oil 0 to 120°C velocity m/s <0.6 | 0.0005
SALT Crude oil 0 to 120°C velocity m/s 0.6-1.2 | 0.0004
SALT Crude oil 0 to 120°C velocity m/s <1.2 | 0.0004
SALT Crude oil 120°C to 180°C velocity m/s <0.6 | 0.0009
SALT Crude oil 120°C to 180°C velocity m/s 0.6-1.2 | 0.0007
SALT Crude oil 120°C to 180°C velocity m/s <1.2 | 0.0007
DRY Crude oil 0 to 120°C velocity m/s <0.6 | 0.0005
DRY Crude oil 0 to 120°C velocity m/s 0.6-1.2 | 0.0004
DRY Crude oil 0 to 120°C velocity m/s <1.2 | 0.0004
DRY Crude oil 120°C to 180°C velocity m/s <0.6 | 0.0005
DRY Crude oil 120°C to 180°C velocity m/s 0.6-1.2 | 0.0004
DRY Crude oil 120°C to 180°C velocity m/s <1.2 | 0.0004
SALT Crude oil 180°C to 230°C velocity m/s <0.6 | 0.001
SALT Crude oil 180°C to 230°C velocity m/s 0.6-1.2 | 0.0009
SALT Crude oil 180°C to 230°C velocity m/s <1.2 | 0.0007
SALT Crude oil 230°C and more velocity m/s <0.6 | 0.0012
SALT Crude oil 230°C and more velocity m/s 0.6-1.2 | 0.001
SALT Crude oil 230°C and more velocity m/s <1.2 | 0.001
DRY Crude oil 180°C to 230°C velocity m/s <0.6 | 0.0007
DRY Crude oil 180°C to 230°C velocity m/s 0.6-1.2 | 0.0005
DRY Crude oil 180°C to 230°C velocity m/s <1.2 | 0.0004
DRY Crude oil 230°C and more velocity m/s <0.6 | 0.0009
DRY Crude oil 230°C and more velocity m/s 0.6-1.2 | 0.0007
DRY Crude oil 230°C and more velocity m/s <1.2 | 0.0007
Gasoline | 0.0004
Naphtha and light distillates | 0.0005
Kerosene | 0.0005
Light gas oil | 0.0005
Heavy gas oil | 0.0005–0.0008
Heavy fuel oils | 0.0008–0.0012
Vacuum tower bottoms | 0.002
Atmosphere tower bottoms | 0.0014
Cracking and coking units - Overhead vapors | 0.0004
Cracking and coking units - Light cycle oil | 0.0004
Cracking and coking units - Heavy cycle oil | 0.0005–0.0007
Fuel oil no. 2 | 0.0004
Fuel oil no. 6 | 0.0009
Transformer oil | 0.0002
Engine lube oil | 0.0002
Quench oil | 0.0007
Refrigerant liquids | 0.0002
Hydraulic fluids | 0.0002
Industrial organic heat transfer media | 0.0002
Molten salts | 9e-05
Ammonia, liquid | 0.0002
Ammonia, liquid (or bearing) | 0.0005
Calcium chloride solutions | 0.0005
Manufactured gas | 0.002
Diesel engine exhaust gas | 0.002
Steam (nonoil bearing) | 9e-05
Exhaust team (oil bearing) | 0.004
Compressed air | 0.002
Refrigerant vapors in refrigerant cycle condensers | 0.004
Ammonia vapor | 0.0002
CO vapor 2 | 0.0002
Chlorine vapor | 0.0004
Coal fuel gas | 0.002
Natural gas flue gas | 0.0009
MEA and DEA solutions | 0.0004
DEG and TEG solutions | 0.0009
Stable side draw and bottom products | 0.0002
Caustic solutions | 0.0004
Vegetable oils | 0.0005
Acid gases | 0.0004
Solvent vapors | 0.0002
Stable overhead products | 0.0002
Crude and vapor unit gases and vapors | 0.0002
Atmospheric tower overhead vapors | 0.0002
Overhead vapors - Cracking and coking unit streams | 0.0004
Light-cycle oil - Cracking and coking unit streams | 0.0004
Heavy-cycle oil - Cracking and coking unit streams | 0.0005–0.0007
Light coker gas oil - Cracking and coking unit streams | 0.0005–0.0007
Heavy coker gas oil - Cracking and coking unit streams | 0.0007–0.0009
Bottom slurry oil (minimum 4.5 ft/s) - Cracking and coking unit streams | 0.0005
Light liquid products - Cracking and coking unit streams | 0.0005
Feed - Naphtha hydrotreater | 0.0005
Effluent - Naphtha hydrotreater | 0.0004
Naphtha - Naphtha hydrotreater | 0.0004
Overhead vapors - Naphtha hydrotreater | 0.0003
Overhead vapor- Visbreaker | 0.0005
Visbreaker bottoms- Visbreaker | 0.0020

## film_heat transfer_coefficients
Column1 | Fluid condition | Typical film heat transfer coefficients (W/m2.K)
Water | Liquid | 5,000-7,500
Ammonia | Liquid | 6,000-8,000
Light organics | Liquid | 1,500-2,000
Medium organics | Liquid | 750-1,500
Heavy organics | Liquid
| Heating | 250-750
| Cooling | 150-400
Very heavy organiés | Liquid
| Heating | 100-300
| Cooling | 60-150
Gas | 1-2 bar abs | 80-125
Gas | 10 bar abs | 250-400
Gas | 100 bar abs | 500-800
Condensing Heat Transfer
Steam, ammonia | No noncondensable | 8,000-12,000
Light organics | Pure component, 0.1 bar abs, no noncondensable | 2,000-5,000
Light organics | 0.1 bar, 4% noncontensable | 750-1,000
Medium organics | Pure or narrow condensing range, 1 bar abs | 1,500-4,000
Heavy organics | Narrow condensing range, 1 bar abs | 600-2,000 .
Light multicomponent mixture, all condensable | Medium condensing range, 1 bar abs | 1,000-2,500
Medium multicomponent mixture, all condensable | Medium condensing range, 1 bar abs | 600-1,500
Heavy multicomponent mixture, all condensable | Medium condensing range, 1 bar abs | 300-600
Vaporizing Heat Transfer
Water | Pressure <5 bar abs, dT = 25 K | 5,000-10,000
Water | Pressure 5-100 bar abs, dT = 20 K | 4,000-15,000
Ammonia | Pressure <30 bar abs, dT = 20 K | 3,000-5,000
Light organics | Pure component, pressure < 30 bar abs, dT = 20 K | 2,000-4,000
Light organics | Narrow bolling range, pressure 20-150 bar abs, dT at 15-20 | 750-3,000
Medium organics | Narrow boiling range, pressure < 20 bar abs,dTmax = 15 K | 600-2,500
Heavy organics | Narrrow boiling range, pressure <20 bar abs, dTmax = 15 K | 400-1,500

## overall_U
Fluids | U (W/m2 K)
Water to water | 1300-2500
Ammonia to water | 1000-2500
Gases to water | 10-250
Water to compressed air | 50-170
Water to lubricating oil | 110-340
Light organics (µ < 5 X 10^-4 Ns/m2) to water | 370-750
Medium organics (5 x 10^-4 < µ < 10x10^-4 Ns/m2 to water | 240-650
Heavy organics (µ > 10 X 10^-4 Ns/m2 to lubricating oil | 25-400
Steam to water | 2200-3500
Steam to ammonia | 1000-3400
Water to condensing ammonia | 850-1500
Water to boiling Freon-12 | 280-1000
Steam to gases | 25-240
Steam to light organics | 490-1000
Steam to medium organics | 250-500
Steam to heavy organics | 30-300
Light organics to light organics | 200-350
Medium organics to medium organics | 100-300
Heavy organics to heavy organics | 50-200
Light organics to heavy organics | 50-200
Heavy organics to light organics | 150-300
Crude oil to gas oil | 130-320
Plate heat exchangers: water to water | 3000-4000
Evaporators: steam/water | 1500-6000
Evaporators: steam/other fluids | 300-2000
Evaporators of refrigeration | 300-1000
Condensers: steam/water | 1000-4000
Condensers: steam/other fluids | 300-1000
Gas boiler | 10-50
Oil bath for heating | 30-550

## Tube_count
Tubesheet type and no. of passes | tube size and pitch | 8 | 10 | 12 | 13 ¼ | 15 ¼ | 17 ¼ | 19 ¼ | 21 ¼ | 23 ¼ | 25 | 27 | 29 | 31 | 33 | 35 | 37
Fixed Tubes One-Pass | ¾ in. on 15/ 16 in ∆ | 33 | 69 | 105 | 135 | 193 | 247 | 307 | 391 | 481 | 553 | 663 | 763 | 881 | 1019 | 1143 | 1,269
Fixed Tubes One-Pass | ¾ in. on 1in. ∆ | 33 | 57 | 91 | 117 | 157 | 217 | 277 | 343 | 423 | 493 | 577 | 667 | 765 | 889 | 1007 | 1,127
Fixed Tubes One-Pass | ¾ in. on 1in ◽ | 33 | 53 | 85 | 101 | 139 | 183 | 235 | 287 | 355 | 419 | 495 | 587 | 665 | 765 | 865 | 965
Fixed Tubes One-Pass | 1 in. on ¼ in. ∆ | 15 | 33 | 57 | 73 | 103 | 133 | 163 | 205 | 247 | 307 | 361 | 427 | 481 | 551 | 633 | 699
Fixed Tubes One-Pass | 1 in. on 1 ¼ in ◽ | 17 | 33 | 45 | 65 | 83 | 111 | 139 | 179 | 215 | 255 | 303 | 359 | 413 | 477 | 545 | 595
Fixed Tubes Two-Pass | ¾ in. on 15/ 16 in ∆ | 32 | 58 | 94 | 124 | 166 | 228 | 300 | 370 | 452 | 528 | 626 | 734 | 846 | 964 | 1088 | 1242
Fixed Tubes Two-Pass | ¾ in. on 1 in. ∆ | 28 | 56 | 90 | 110 | 154 | 208 | 264 | 326 | 398 | 468 | 556 | 646 | 746 | 858 | 972 | 1,088
Fixed Tubes Two-Pass | ¾ in. on 1 in ◽ | 26 | 48 | 78 | 94 | 126 | 172 | 222 | 280 | 346 | 408 | 486 | 560 | 644 | 746 | 840 | 946
Fixed Tubes Two-Pass | 1 in. on 1 ¼ in ∆ | 16 | 32 | 52 | 62 | 92 | 126 | 162 | 204 | 244 | 292 | 346 | 410 | 462 | 530 | 608 | 688
Fixed Tubes Two-Pass | 1 in. on 1 ¼ in ◽ | 12 | 26 | 40 | 56 | 76 | 106 | 136 | 172 | 218 | 248 | 298 | 348 | 402 | 460 | 522 | 584
U Tubes Two-Pass | ¾ in. on 15/ 16 in ∆ | 8 | 34 | 64 | 94 | 134 | 180 | 234 | 304 | 398 | 460 | 558 | 648 | 768 | 882 | 1008 | 1,126
U Tubes Two-Pass | ¾ in. on 1in. ∆ | 8 | 26 | 60 | 72 | 108 | 158 | 212 | 270 | 336 | 406 | 484 | 566 | 674 | 772 | 882 | 1,000
U Tubes Two-Pass | ¾ in. on 1in ◽ | 12 | 30 | 52 | 72 | 100 | 142 | 188 | 242 | 304 | 362 | 436 | 506 | 586 | 688 | 778 | 884
U Tubes Two-Pass | 1 in. on 1 ¼ in ∆ | XX | 8 | 26 | 42 | 58 | 84 | 120 | 154 | 192 | 234 | 284 | 340 | 396 | 466 | 532 | 610
U Tubes Two-Pass | 1 in. on 1 ¼ in ◽ | XX | 12 | 22 | 38 | 58 | 76 | 100 | 134 | 180 | 214 | 256 | 304 | 356 | 406 | 464 | 526
Fixed Tubes Four-Pass | ¾ in. on 15/ 16 in ∆ | XX | 48 | 84 | 108 | 154 | 196 | 266 | 332 | 412 | 484 | 576 | 680 | 788 | 904 | 1024 | 1,072
Fixed Tubes Four-Pass | ¾ in. on 1in. ∆ | XX | 44 | 72 | 96 | 134 | 180 | 232 | 292 | 360 | 424 | 508 | 596 | 692 | 802 | 912 | 1,024
Fixed Tubes Four-Pass | ¾ in. on 1in ◽ | XX | 48 | 72 | 88 | 126 | 142 | 192 | 242 | 308 | 366 | 440 | 510 | 590 | 688 | 778 | 880
Fixed Tubes Four-Pass | 1 in. on 1 ¼ in ∆ | XX | 24 | 44 | 60 | 78 | 104 | 138 | 176 | 212 | 258 | 308 | 368 | 422 | 486 | 560 | 638
Fixed Tubes Four-Pass | 1 in. on 1 ¼ in ◽ | XX | 24 | 40 | 48 | 74 | 84 | 110 | 142 | 188 | 214 | 260 | 310 | 360 | 414 | 476 | 534
U Tubes Four-Pass | ¾ in. on 15/ 16 in ∆ | XX | 28 | 56 | 84 | 122 | 166 | 218 | 286 | 378 | 438 | 534 | 622 | 740 | 852 | 976 | 1,092
U Tubes Four-Pass | ¾ in. on 1in. ∆ | XX | 20 | 52 | 64 | 98 | 146 | 198 | 254 | 318 | 386 | 462 | 542 | 648 | 744 | 852 | 968
U Tubes Four-Pass | ¾ in. on 1in ◽ | XX | 24 | 44 | 64 | 90 | 130 | 174 | 226 | 286 | 342 | 414 | 482 | 560 | 660 | 748 | 852
U Tubes Four-Pass | 1 in. on 1 ¼ in ∆ | XX | XX | 20 | 36 | 50 | 74 | 110 | 142 | 178 | 218 | 266 | 322 | 376 | 444 | 508 | 584
U Tubes Four-Pass | 1 in. on 1 ¼ in ◽ | XX | XX | 16 | 32 | 50 | 66 | 90 | 122 | 166 | 198 | 238 | 286 | 336 | 384 | 440 | 500
Fixed Tubes Six-Pass | ¾ in. on 15/ 16 in ∆ | XX | XX | XX | 80 | 116 | 174 | 230 | 294 | 372 | 440 | 532 | 632 | 732 | 844 | 964 | 1,106
Fixed Tubes Six-Pass | ¾ in. on 1in. ∆ | XX | XX | XX | 66 | 104 | 156 | 202 | 258 | 322 | 388 | 464 | 548 | 640 | 744 | 852 | 964
Fixed Tubes Six-Pass | ¾ in. on 1in ◽ | XX | XX | XX | 54 | 78 | 116 | 158 | 212 | 266 | 324 | 394 | 460 | 536 | 634 | 224 | 818
Fixed Tubes Six-Pass | 1 in. on 1 ¼ in ∆ | XX | XX | XX | 34 | 56 | 82 | 112 | 150 | 182 | 226 | 274 | 338 | 382 | 442 | 514 | 586
Fixed Tubes Six-Pass | 1 in. on 1 ¼ in ◽ | XX | XX | XX | XX | 44 | 66 | 88 | 116 | 154 | 184 | 226 | 268 | 318 | 368 | 430 | 484
U Tubes Six-Pass | ¾ in. on 15/ 16 in ∆ | XX | XX | XX | 74 | 110 | 156 | 206 | 272 | 358 | 416 | 510 | 596 | 716 | 826 | 944 | 1,058
U Tubes Six-Pass | ¾ in. on 1in. ∆ | XX | XX | XX | 56 | 88 | 134 | 184 | 238 | 300 | 366 | 440 | 518 | 626 | 720 | 826 | 940
U Tubes Six-Pass | ¾ in. on 1in ◽ | XX | XX | XX | 56 | 80 | 118 | 160 | 210 | 268 | 322 | 392 | 458 | 534 | 632 | 718 | 820
U Tubes Six-Pass | 1 in. on 1 ¼ in ∆ | XX | XX | XX | 30 | 42 | 68 | 100 | 130 | 168 | 206 | 252 | 304 | 356 | 426 | 488 | 562
U Tubes Six-Pass | 1 in. on 1 ¼ in ◽ | XX | XX | XX | XX | 42 | 60 | 80 | 110 | 152 | 182 | 224 | 268 | 316 | 362 | 420 | 478
Fixed Tubes eight-Pass | ¾ in. on 15/ 16 in ∆ | XX | XX | XX | XX | 94 | 140 | 198 | 258 | 332 | 398 | 484 | 576 | 682 | 790 | 902 | 1,040
Fixed Tubes eight-Pass | ¾ in. on 1in. ∆ | XX | XX | XX | XX | 82 | 124 | 170 | 224 | 286 | 344 | 422 | 496 | 588 | 694 | 798 | 902
Fixed Tubes eight-Pass | ¾ in. on 1in ◽ | XX | XX | XX | XX | XX | 94 | 132 | 174 | 228 | 286 | 352 | 414 | 490 | 576 | 662 | 760
Fixed Tubes eight-Pass | 1 in. on 1 ¼ in ∆ | XX | XX | XX | XX | XX | 66 | 90 | 120 | 154 | 190 | 240 | 298 | 342 | 400 | 466 | 542
Fixed Tubes eight-Pass | 1 in. on 1 ¼ in ◽ | XX | XX | XX | XX | XX | XX | 74 | 94 | 128 | 150 | 192 | 230 | 280 | 334 | 388 | 438
U Tubes eight-Pass | ¾ in. on 15/ 16 in ∆ | XX | XX | XX | 68 | 102 | 142 | 190 | 254 | 342 | 398 | 490 | 578 | 688 | 796 | 916 | 1,032
U Tubes eight-Pass | ¾ in. on 1in. ∆ | XX | XX | XX | 52 | 82 | 122 | 170 | 226 | 286 | 350 | 422 | 498 | 600 | 692 | 796 | 908
U Tubes eight-Pass | ¾ in. on 1in ◽ | XX | XX | XX | 48 | 70 | 106 | 146 | 194 | 254 | 306 | 374 | 438 | 512 | 608 | 692 | 792
U Tubes eight-Pass | 1 in. on 1 ¼ in ∆ | XX | XX | XX | 24 | 38 | 58 | 90 | 118 | 154 | 190 | 238 | 290 | 340 | 404 | 464 | 540
U Tubes eight-Pass | 1 in. on 1 ¼ in ◽ | XX | XX | XX | XX | 34 | 50 | 70 | 98 | 142 | 170 | 206 | 254 | 300 | 344 | 396 | 456
TEMA P or S One-Pass | 1.25 in. on 1 9/16 in ◽ | 12 | 21 | 29 | 38 | 52 | 70 | 85 | 108 | 136 | 154 | 184 | 217 | 252 | 289 | 329 | 372
TEMA P or S Two-Pass | 1.25 in. on 1 9/16 in ◽ | 12 | 12 | 28 | 34 | 48 | 66 | 84 | 108 | 128 | 154 | 180 | 212 | 248 | 276 | 316 | 368
TEMA P or S Four-Pass | 1.25 in. on 1 9/16 in ◽ | 4 | 8 | 16 | 34 | 44 | 56 | 70 | 100 | 128 | 142 | 158 | 204 | 234 | 270 | 310 | 354
TEMA P or S Six-Pass | 1.25 in. on 1 9/16 in ◽ | 0 | 12 | 18 | 24 | 48 | 50 | 80 | 96 | 114 | 136 | 172 | 198 | 236 | 264 | 304 | 340
U Tubes Two-Pass | 1.25 in. on 1 9/16 in ◽ | 4 | 12 | 26 | 36 | 44 | 60 | 82 | 100 | 128 | 154 | 176 | 212 | 242 | 280 | 324 | 358
U Tubes Four-Pass | 1.25 in. on 1 9/16 in ◽ | 4 | 8 | 20 | 28 | 44 | 60 | 76 | 100 | 120 | 148 | 172 | 204 | 240 | 280 | 312 | 352
U Tubes Six-Pass | 1.25 in. on 1 9/16 in ◽ | 6 | 12 | 12 | 15 | 32 | 56 | 79 | 100 | 120 | 130 | 160 | 198 | 234 | 274 | 308 | 350
TEMA L or M One-Pass | 1.25 in. on 1 9/16 in ∆ | 15 | 27 | 38 | 55 | 66 | 88 | 117 | 136 | 170 | 198 | 237 | 268 | 312 | 357 | 417 | 446
TEMA L or M Two-Pass | 1.25 in. on 1 9/16 in ∆ | 10 | 22 | 36 | 44 | 64 | 82 | 106 | 134 | 164 | 188 | 228 | 266 | 304 | 346 | 396 | 446
TEMA L or M Four-Pass | 1.25 in. on 1 9/16 in ∆ | 8 | 16 | 26 | 42 | 52 | 78 | 98 | 124 | 146 | 166 | 208 | 242 | 284 | 322 | 372 | 422
TEMA L or M Six-Pass | 1.25 in. on 1 9/16 in ∆ | 12 | 12 | 24 | 40 | 50 | 68 | 96 | 108 | 148 | 168 | 192 | 236 | 276 | 324 | 364 | 408
TEMA P or S One-Pass | 1.25 in. on 1 9/16 in ∆ | 13 | 18 | 33 | 38 | 57 | 81 | 100 | 126 | 159 | 183 | 208 | 249 | 291 | 333 | 372 | 425
TEMA P or S Two-Pass | 1.25 in. on 1 9/16 in ∆ | 10 | 20 | 26 | 44 | 58 | 72 | 94 | 120 | 146 | 172 | 206 | 238 | 282 | 326 | 368 | 412
TEMA P or S Four-Pass | 1.25 in. on 1 9/16 in ∆ | 4 | 8 | 26 | 34 | 48 | 62 | 86 | 116 | 132 | 150 | 190 | 224 | 262 | 298 | 344 | 394
TEMA P or S Six-Pass | 1.25 in. on 1 9/16 in ∆ | 0 | 12 | 18 | 24 | 44 | 68 | 80 | 102 | 132 | 148 | 180 | 220 | 256 | 296 | 336 | 384
U Tubes Two-Pass | 1.25 in. on 1 9/16 in ∆ | 6 | 14 | 28 | 34 | 52 | 72 | 90 | 118 | 148 | 172 | 200 | 242 | 282 | 326 | 362 | 416
U Tubes Four-Pass | 1.25 in. on 1 9/16 in ∆ | 4 | 12 | 20 | 28 | 48 | 68 | 84 | 112 | 132 | 160 | 188 | 228 | 264 | 308 | 344 | 396
U Tubes Six-Pass | 1.25 in. on 1 9/16 in ∆ | 6 | 12 | 18 | 30 | 40 | 64 | 78 | 102 | 120 | 152 | 180 | 216 | 250 | 292 | 336 | 384