## fouling_factors
Stream | fouling factors
Natural gas | 0.0002–0.0004
Column verhead products | 0.0002
Lean oil | 0.0004
Rich oil | 0.0002
Natural gasoline and liquefied petroleum gases | 0.0002
Atmospheric tower overhead vapors | 0.0002
Light Naphtha | 0.0004
Vacuum overhead vapors | 0.0008
SALT Crude oil 0 to 120°C velocity m/s <0.6 | 0.0005
SALT Crude oil 0 to 120°C velocity m/s 0.6-1.2 | 0.0004
SALT Crude oil 0 to 120°C velocity m/s <1.2 | 0.0004
SALT Crude oil 120°C to 180°C velocity m/s <0.6 | 0.0009
SALT Crude oil 120°C to 180°C velocity m/s 0.6-1.2 | 0.0007
SALT Crude oil 120°C to 180°C velocity m/s <1.2 | 0.0007
DRY Crude oil 0 to 120°C velocity m/s <0.6 | 0.0005
DRY Crude oil 0 to 120°C velocity m/s 0.6-1.2 | 0.0004
DRY Crude oil 0 to 120°C velocity m/s <1.2 | 0.0004
DRY Crude oil 120°C to 180°C velocity m/s <0.6 | 0.0005
DRY Crude oil 120°C to 180°C velocity m/s 0.6-1.2 | 0.0004
DRY Crude oil 120°C to 180°C velocity m/s <1.2 | 0.0004
SALT Crude oil 180°C to 230°C velocity m/s <0.6 | 0.001
SALT Crude oil 180°C to 230°C velocity m/s 0.6-1.2 | 0.0009
SALT Crude oil 180°C to 230°C velocity m/s <1.2 | 0.0007
SALT Crude oil 230°C and more velocity m/s <0.6 | 0.0012
SALT Crude oil 230°C and more velocity m/s 0.6-1.2 | 0.001
SALT Crude oil 230°C and more velocity m/s <1.2 | 0.001
DRY Crude oil 180°C to 230°C velocity m/s <0.6 | 0.0007
DRY Crude oil 180°C to 230°C velocity m/s 0.6-1.2 | 0.0005
DRY Crude oil 180°C to 230°C velocity m/s <1.2 | 0.0004
DRY Crude oil 230°C and more velocity m/s <0.6 | 0.0009
DRY Crude oil 230°C and more velocity m/s 0.6-1.2 | 0.0007
DRY Crude oil 230°C and more velocity m/s <1.2 | 0.0007
Gasoline | 0.0004
Naphtha and light distillates | 0.0005
Kerosene | 0.0005
Light gas oil | 0.0005
Heavy gas oil | 0.0005–0.0008
Heavy fuel oils | 0.0008–0.0012
Vacuum tower bottoms | 0.002
Atmosphere tower bottoms | 0.0014
Cracking and coking units - Overhead vapors | 0.0004
Cracking and coking units - Light cycle oil | 0.0004
Cracking and coking units - Heavy cycle oil | 0.0005–0.0007
Fuel oil no. 2 | 0.0004
Fuel oil no. 6 | 0.0009
Transformer oil | 0.0002
Engine lube oil | 0.0002
Quench oil | 0.0007
Refrigerant liquids | 0.0002
Hydraulic fluids | 0.0002
Industrial organic heat transfer media | 0.0002
Molten salts | 9e-05
Ammonia, liquid | 0.0002
Ammonia, liquid (or bearing) | 0.0005
Calcium chloride solutions | 0.0005
Manufactured gas | 0.002
Diesel engine exhaust gas | 0.002
Steam (nonoil bearing) | 9e-05
Exhaust team (oil bearing) | 0.004
Compressed air | 0.002
Refrigerant vapors in refrigerant cycle condensers | 0.004
Ammonia vapor | 0.0002
CO vapor 2 | 0.0002
Chlorine vapor | 0.0004
Coal fuel gas | 0.002
Natural gas flue gas | 0.0009
MEA and DEA solutions | 0.0004
DEG and TEG solutions | 0.0009
Stable side draw and bottom products | 0.0002
Caustic solutions | 0.0004
Vegetable oils | 0.0005
Acid gases | 0.0004
Solvent vapors | 0.0002
Stable overhead products | 0.0002
Crude and vapor unit gases and vapors | 0.0002
Atmospheric tower overhead vapors | 0.0002
Overhead vapors - Cracking and coking unit streams | 0.0004
Light-cycle oil - Cracking and coking unit streams | 0.0004
Heavy-cycle oil - Cracking and coking unit streams | 0.0005–0.0007
Light coker gas oil - Cracking and coking unit streams | 0.0005–0.0007
Heavy coker gas oil - Cracking and coking unit streams | 0.0007–0.0009
Bottom slurry oil (minimum 4.5 ft/s) - Cracking and coking unit streams | 0.0005
Light liquid products - Cracking and coking unit streams | 0.0005
Feed - Naphtha hydrotreater | 0.0005
Effluent - Naphtha hydrotreater | 0.0004
Naphtha - Naphtha hydrotreater | 0.0004
Overhead vapors - Naphtha hydrotreater | 0.0003
Overhead vapor- Visbreaker | 0.0005
Visbreaker bottoms- Visbreaker | 0.0020

## film_heat transfer_coefficients
Column1 | Fluid condition | Typical film heat transfer coefficients (W/m2.K)
Water | Liquid | 5,000-7,500
Ammonia | Liquid | 6,000-8,000
Light organics | Liquid | 1,500-2,000
Medium organics | Liquid | 750-1,500
Heavy organics | Liquid
| Heating | 250-750
| Cooling | 150-400
Very heavy organiés | Liquid
| Heating | 100-300
| Cooling | 60-150
Gas | 1-2 bar abs | 80-125
Gas | 10 bar abs | 250-400
Gas | 100 bar abs | 500-800
Condensing Heat Transfer
Steam, ammonia | No noncondensable | 8,000-12,000
Light organics | Pure component, 0.1 bar abs, no noncondensable | 2,000-5,000
Light organics | 0.1 bar, 4% noncontensable | 750-1,000
Medium organics | Pure or narrow condensing range, 1 bar abs | 1,500-4,000
Heavy organics | Narrow condensing range, 1 bar abs | 600-2,000 .
Light multicomponent mixture, all condensable | Medium condensing range, 1 bar abs | 1,000-2,500
Medium multicomponent mixture, all condensable | Medium condensing range, 1 bar abs | 600-1,500
Heavy multicomponent mixture, all condensable | Medium condensing range, 1 bar abs | 300-600
Vaporizing Heat Transfer
Water | Pressure <5 bar abs, dT = 25 K | 5,000-10,000
Water | Pressure 5-100 bar abs, dT = 20 K | 4,000-15,000
Ammonia | Pressure <30 bar abs, dT = 20 K | 3,000-5,000
Light organics | Pure component, pressure < 30 bar abs, dT = 20 K | 2,000-4,000
Light organics | Narrow bolling range, pressure 20-150 bar abs, dT at 15-20 | 750-3,000
Medium organics | Narrow boiling range, pressure < 20 bar abs,dTmax = 15 K | 600-2,500
Heavy organics | Narrrow boiling range, pressure <20 bar abs, dTmax = 15 K | 400-1,500

## overall_U
Fluids | U (W/m2 K)
Water to water | 1300-2500
Ammonia to water | 1000-2500
Gases to water | 10-250
Water to compressed air | 50-170
Water to lubricating oil | 110-340
Light organics (µ < 5 X 10^-4 Ns/m2) to water | 370-750
Medium organics (5 x 10^-4 < µ < 10x10^-4 Ns/m2 to water | 240-650
Heavy organics (µ > 10 X 10^-4 Ns/m2 to lubricating oil | 25-400
Steam to water | 2200-3500
Steam to ammonia | 1000-3400
Water to condensing ammonia | 850-1500
Water to boiling Freon-12 | 280-1000
Steam to gases | 25-240
Steam to light organics | 490-1000
Steam to medium organics | 250-500
Steam to heavy organics | 30-300
Light organics to light organics | 200-350
Medium organics to medium organics | 100-300
Heavy organics to heavy organics | 50-200
Light organics to heavy organics | 50-200
Heavy organics to light organics | 150-300
Crude oil to gas oil | 130-320
Plate heat exchangers: water to water | 3000-4000
Evaporators: steam/water | 1500-6000
Evaporators: steam/other fluids | 300-2000
Evaporators of refrigeration | 300-1000
Condensers: steam/water | 1000-4000
Condensers: steam/other fluids | 300-1000
Gas boiler | 10-50
Oil bath for heating | 30-550

## Tube_count
Do | pitch layout | pitch | TEMA type | (Internal Shell Diameter) in | (Internal Shell Diameter) mm | (Number of Tube Passes) 1 | (Number of Tube Passes) 2 | (Number of Tube Passes) 4 | (Number of Tube Passes) 6
19.05 | Triangular 30 | 25.4 | L | 8 | 203.2 | 38 | 36 | 32 | 24
19.05 | Triangular 30 | 25.4 | L | 10 | 254 | 69 | 62 | 56 | 48
19.05 | Triangular 30 | 25.4 | L | 12 | 304.8 | 105 | 94 | 88 | 76
19.05 | Triangular 30 | 25.4 | L | 13.25 | 336.5 | 129 | 120 | 108 | 104
19.05 | Triangular 30 | 25.4 | L | 15.25 | 387.3 | 181 | 166 | 154 | 148
19.05 | Triangular 30 | 25.4 | L | 17.25 | 438.15 | 235 | 218 | 206 | 198
19.05 | Triangular 30 | 25.4 | L | 19.25 | 488.9 | 295 | 280 | 262 | 252
19.05 | Triangular 30 | 25.4 | L | 21.25 | 539.7 | 356 | 344 | 330 | 314
19.05 | Triangular 30 | 25.4 | L | 23.25 | 590.5 | 431 | 418 | 398 | 388
19.05 | Triangular 30 | 25.4 | L | 25 | 635 | 504 | 492 | 462 | 446
19.05 | Triangular 30 | 25.4 | L | 27 | 685.8 | 597 | 578 | 550 | 538
19.05 | Triangular 30 | 25.4 | L | 29 | 736.6 | 694 | 674 | 646 | 634
19.05 | Triangular 30 | 25.4 | L | 31 | 787.4 | 799 | 778 | 750 | 732
19.05 | Triangular 30 | 25.4 | L | 33 | 838.2 | 919 | 888 | 854 | 834
19.05 | Triangular 30 | 25.4 | L | 35 | 889 | 1031 | 1004 | 968 | 946
19.05 | Triangular 30 | 25.4 | L | 37 | 939.8 | 1149 | 1128 | 1084 | 1052
19.05 | Triangular 30 | 25.4 | L | 39 | 990.6 | 1284 | 1258 | 1216 | 1202
19.05 | Triangular 30 | 25.4 | L | 42 | 1066.8 | 1499 | 1452 | 1416 | 1382
19.05 | Triangular 30 | 25.4 | L | 45 | 1143 | 1727 | 1686 | 1640 | 1616
19.05 | Square 90 | 25.4 | U | 8 | 203.2 |  | 26 | 20 | 20
19.05 | Square 90 | 25.4 | U | 10 | 254 |  | 48 | 44 | 40
19.05 | Square 90 | 25.4 | U | 12 | 304.8 |  | 74 | 68 | 68
19.05 | Square 90 | 25.4 | U | 13.25 | 336.5 |  | 94 | 88 | 84
19.05 | Square 90 | 25.4 | U | 15.25 | 387.3 |  | 126 | 122 | 114
19.05 | Square 90 | 25.4 | U | 17.25 | 438.15 |  | 172 | 170 | 160
19.05 | Square 90 | 25.4 | U | 19.25 | 488.9 |  | 218 | 218 | 218
19.05 | Square 90 | 25.4 | U | 21.25 | 539.7 |  | 280 | 278 | 268
19.05 | Square 90 | 25.4 | U | 23.25 | 590.5 |  | 346 | 338 | 330
19.05 | Square 90 | 25.4 | U | 25 | 635 |  | 408 | 390 | 386
19.05 | Square 90 | 25.4 | U | 27 | 685.8 |  | 478 | 470 | 454
19.05 | Square 90 | 25.4 | U | 29 | 736.6 |  | 560 | 546 | 534
19.05 | Square 90 | 25.4 | U | 31 | 787.4 |  | 646 | 634 | 618
19.05 | Square 90 | 25.4 | U | 33 | 838.2 |  | 744 | 730 | 716
19.05 | Square 90 | 25.4 | U | 35 | 889 |  | 840 | 820 | 816
19.05 | Square 90 | 25.4 | U | 37 | 939.8 |  | 946 | 932 | 918
19.05 | Square 90 | 25.4 | U | 39 | 990.6 |  | 1060 | 1048 | 1032
19.05 | Square 90 | 25.4 | U | 42 | 1066.8 |  | 1240 | 1220 | 1192
19.05 | Square 90 | 25.4 | U | 45 | 1143 |  | 1430 | 1404 | 1388
19.05 | Square 90 | 25.4 | S | 8 | 203.2 |  | 22 | 20 | 18
19.05 | Square 90 | 25.4 | S | 10 | 254 |  | 40 | 40 | 36
19.05 | Square 90 | 25.4 | S | 12 | 304.8 |  | 70 | 64 | 70
19.05 | Square 90 | 25.4 | S | 13.25 | 336.5 |  | 90 | 84 | 84
19.05 | Square 90 | 25.4 | S | 15.25 | 387.3 |  | 126 | 114 | 114
19.05 | Square 90 | 25.4 | S | 17.25 | 438.15 |  | 164 | 158 | 156
19.05 | Square 90 | 25.4 | S | 19.25 | 488.9 |  | 218 | 210 | 198
19.05 | Square 90 | 25.4 | S | 21.25 | 539.7 |  | 268 | 262 | 260
19.05 | Square 90 | 25.4 | S | 23.25 | 590.5 |  | 334 | 326 | 314
19.05 | Square 90 | 25.4 | S | 25 | 635 |  | 392 | 378 | 364
19.05 | Square 90 | 25.4 | S | 27 | 685.8 |  | 462 | 450 | 426
19.05 | Square 90 | 25.4 | S | 29 | 736.6 |  | 544 | 534 | 510
19.05 | Square 90 | 25.4 | S | 31 | 787.4 |  | 634 | 610 | 594
19.05 | Square 90 | 25.4 | S | 33 | 838.2 |  | 716 | 702 | 674
19.05 | Square 90 | 25.4 | S | 35 | 889 |  | 816 | 796 | 780
19.05 | Square 90 | 25.4 | S | 37 | 939.8 |  | 914 | 896 | 882
19.05 | Square 90 | 25.4 | S | 39 | 990.6 |  | 1028 | 1012 | 988
19.05 | Square 90 | 25.4 | S | 42 | 1066.8 |  | 1194 | 1168 | 1156
19.05 | Square 90 | 25.4 | S | 45 | 1143 |  | 1390 | 1364 | 1336
25.4 | Square 90 | 31.75 | U | 8 | 203.2 |  | 12 | 8
25.4 | Square 90 | 31.75 | U | 10 | 254 |  | 26 | 20 | 20
25.4 | Square 90 | 31.75 | U | 12 | 304.8 |  | 40 | 36 | 28
25.4 | Square 90 | 31.75 | U | 13.25 | 336.5 |  | 56 | 48 | 48
25.4 | Square 90 | 31.75 | U | 15.25 | 387.3 |  | 76 | 70 | 66
25.4 | Square 90 | 31.75 | U | 17.25 | 438.15 |  | 102 | 98 | 94
25.4 | Square 90 | 31.75 | U | 19.25 | 488.9 |  | 126 | 130 | 118
25.4 | Square 90 | 31.75 | U | 21.25 | 539.7 |  | 164 | 166 | 156
25.4 | Square 90 | 31.75 | U | 23.25 | 590.5 |  | 206 | 202 | 198
25.4 | Square 90 | 31.75 | U | 25 | 635 |  | 248 | 242 | 232
25.4 | Square 90 | 31.75 | U | 27 | 685.8 |  | 294 | 282 | 274
25.4 | Square 90 | 31.75 | U | 29 | 736.6 |  | 346 | 334 | 322
25.4 | Square 90 | 31.75 | U | 31 | 787.4 |  | 400 | 390 | 382
25.4 | Square 90 | 31.75 | U | 33 | 838.2 |  | 458 | 446 | 438
25.4 | Square 90 | 31.75 | U | 35 | 889 |  | 522 | 508 | 496
25.4 | Square 90 | 31.75 | U | 37 | 939.8 |  | 584 | 576 | 548
25.4 | Square 90 | 31.75 | U | 39 | 990.6 |  | 648 | 648 | 628
25.4 | Square 90 | 31.75 | U | 42 | 1066.8 |  | 758 | 744 | 742
25.4 | Square 90 | 31.75 | U | 45 | 1143 |  | 898 | 880 | 854
19.05 | Square 90 | 31.75 | S | 8 | 203.2 |  | 12 | 8
19.05 | Square 90 | 31.75 | S | 10 | 254 |  | 26 | 24 | 22
19.05 | Square 90 | 31.75 | S | 12 | 304.8 |  | 40 | 40 | 36
19.05 | Square 90 | 31.75 | S | 13.25 | 336.5 |  | 56 | 48 | 48
19.05 | Square 90 | 31.75 | S | 15.25 | 387.3 |  | 76 | 70 | 66
19.05 | Square 90 | 31.75 | S | 17.25 | 438.15 |  | 102 | 98 | 94
19.05 | Square 90 | 31.75 | S | 19.25 | 488.9 |  | 126 | 130 | 118
19.05 | Square 90 | 31.75 | S | 21.25 | 539.7 |  | 164 | 166 | 156
19.05 | Square 90 | 31.75 | S | 23.25 | 590.5 |  | 206 | 202 | 198
19.05 | Square 90 | 31.75 | S | 25 | 635 |  | 248 | 242 | 232
19.05 | Square 90 | 31.75 | S | 27 | 685.8 |  | 294 | 282 | 274
19.05 | Square 90 | 31.75 | S | 29 | 736.6 |  | 346 | 334 | 322
19.05 | Square 90 | 31.75 | S | 31 | 787.4 |  | 400 | 390 | 382
19.05 | Square 90 | 31.75 | S | 33 | 838.2 |  | 458 | 446 | 438
19.05 | Square 90 | 31.75 | S | 35 | 889 |  | 522 | 508 | 496
19.05 | Square 90 | 31.75 | S | 37 | 939.8 |  | 584 | 576 | 548
19.05 | Square 90 | 31.75 | S | 39 | 990.6 |  | 648 | 648 | 628
19.05 | Square 90 | 31.75 | S | 42 | 1066.8 |  | 758 | 744 | 742
19.05 | Square 90 | 31.75 | S | 45 | 1143 |  | 898 | 880 | 854
25.4 | Triangular 30 | 31.75 | L | 8 | 203.2 | 22 | 22 | 12 | 12
25.4 | Triangular 30 | 31.75 | L | 10 | 254 | 40 | 36 | 32 | 28
25.4 | Triangular 30 | 31.75 | L | 12 | 304.8 | 61 | 58 | 48 | 48
25.4 | Triangular 30 | 31.75 | L | 13.25 | 336.5 | 81 | 72 | 68 | 58
25.4 | Triangular 30 | 31.75 | L | 15.25 | 387.3 | 104 | 100 | 94 | 82
25.4 | Triangular 30 | 31.75 | L | 17.25 | 438.15 | 145 | 132 | 122 | 114
25.4 | Triangular 30 | 31.75 | L | 19.25 | 488.9 | 181 | 174 | 162 | 152
25.4 | Triangular 30 | 31.75 | L | 21.25 | 539.7 | 224 | 218 | 202 | 198
25.4 | Triangular 30 | 31.75 | L | 23.25 | 590.5 | 270 | 264 | 246 | 242
25.4 | Triangular 30 | 31.75 | L | 25 | 635 | 317 | 306 | 286 | 280
25.4 | Triangular 30 | 31.75 | L | 27 | 685.8 | 376 | 362 | 338 | 328
25.4 | Triangular 30 | 31.75 | L | 29 | 736.6 | 431 | 414 | 398 | 388
25.4 | Triangular 30 | 31.75 | L | 31 | 787.4 | 500 | 492 | 462 | 458
25.4 | Triangular 30 | 31.75 | L | 33 | 838.2 | 571 | 556 | 530 | 510
25.4 | Triangular 30 | 31.75 | L | 35 | 889 | 641 | 630 | 604 | 582
25.4 | Triangular 30 | 31.75 | L | 37 | 939.8 | 737 | 708 | 680 | 664
25.4 | Triangular 30 | 31.75 | L | 39 | 990.6 | 813 | 796 | 764 | 748
25.4 | Triangular 30 | 31.75 | L | 42 | 1066.8 | 941 | 918 | 888 | 868
25.4 | Triangular 30 | 31.75 | L | 45 | 1143 | 1091 | 1068 | 1028 | 1008